# MicroHydroV1 — Go/No-Go Packet (ASAP Draft)

Executive Summary: This packet aggregates Stage B (bench) and Stage C (electrical/power) evidence for an expedited Go decision. Baseline tests are green per current samples; Stage B matrix and Stage C broadening are planned in the attached timeline.

# 1. Acceptance Criteria (Quick Reference)

| Test | Requirement | Status (to-date) |
| --- | --- | --- |
| T‑001 Jet Coherence | Coherence ≥ 0.90 | PASS on initial samples |
| T‑002 Tank Ripple | −30–50% vs straight inlet; no entrainment increase | PASS on initial samples |
| T‑003 Electrical Stability | Drift ≤ 0.1 Hz; no hunting | PASS on initial samples |
| T‑004 Power Output | 10–12 kW band | PASS on initial samples |

# 2. Evidence Links & Plots

• Bench: ΔP–Q sweeps by vane angle & head — attach plots from RnD workbook/dashboard and intake CSVs

• T‑001: Coherence vs time (plots & raw) — attach plots from RnD workbook/dashboard and intake CSVs

• T‑002: Ripple reduction with baselines — attach plots from RnD workbook/dashboard and intake CSVs

• T‑003: Drift histograms & time series — attach plots from RnD workbook/dashboard and intake CSVs

• T‑004: Power vs time (10–12 kW band) — attach plots from RnD workbook/dashboard and intake CSVs

# 3. Risk Register Snapshot & Mitigations

| Risk | Likelihood | Impact | Mitigation | Trigger |
| --- | --- | --- | --- | --- |
| Clogging at nozzle throat | 2 | 3 | Debris screen; clean per run | Rising ΔP at constant Q |
| Cavitation at high Q | 2 | 4 | Maintain NPSHa ≥ 1 m; round edges | Noise/vibration onset |
| Leak at seals | 2 | 3 | Verify O‑ring compression; grease | Visible drips |
| Instrumentation drift | 2 | 3 | Zero transducers; two‑point check | Baseline shift |

# 4. STW Decisions (Admit/Hold)

| Item | Decision | Evidence Link |
| --- | --- | --- |
| Hyperbolic Tank Inlet (diffuser) | Admit | Link to ΔP–Q & ripple results |
| 9 mm pre‑swirl nozzle | Admit | Link to ΔP–Q & coherence results |
| DN125 penstock baseline | Admit | Bench config + stability notes |
| Conventional narrow ELC window | Admit | ELC drift plots |
| φ‑segmented penstocks | Hold | TBD: extended stability |
| φ‑ELC windows | Hold | TBD: hunting risk downselect |
| Hydram φ‑timing | Hold | TBD: flow ≥ +5% evidence |

# 5. Decision

Recommendation: Provisional GO contingent on closing Stage B matrix and Stage C broadened stability. Final GO on completion of Week‑1/2/3 deliverables in the timeline.

# 6. Timeline (ASAP)

See attached Excel: MicroHydroV1_ASAP_Timeline.xlsx