## Deliverables_A-D
Package | Item

## Stages
Stage | Status | Details

## Artifacts
Name | Stage | Status | Notes

## Acceptance_Criteria
Criterion
Jet coherence ≥ 0.90
Ripple amplitude −30–50% vs straight inlet; no entrainment increase
ELC drift ≤ 0.1 Hz; no hunting
Power 10–12 kW window

## Sections
Section | Title

## Tests
Test_ID | Name | Objective | Setup | Parameters | Instruments | Acceptance_Criteria | Status | Stage | Linked_Artifacts
T-001 | Jet_Coherence_Test | Assess jet coherence; ensure coherent jet meets threshold. | Bench Test Pack; imaging config |  | Imaging setup (per imaging config). | Jet coherence ≥ 0.90 | Defined | B | Procedure; Datasheet; Imaging config
T-002 | Tank_Ripple_Test | Measure tank ripple amplitude reduction vs straight inlet; verify no entrainment increase. | Bench Test Pack; PT mounting sketch |  | Pressure transducer (PT). | Ripple amplitude −30–50% vs straight inlet; no entrainment increase | Defined | B | Procedure; Datasheet; PT mounting sketch
T-003 | Electrical_Stability | Verify ELC drift ≤ 0.1 Hz with no hunting | Generator + ELC narrow window; nominal load |  | ELC + scope/logger | ELC drift ≤ 0.1 Hz; no hunting | Defined | C | Procedure; Logger config
T-004 | Power_Output | Confirm power within 10–12 kW at operating head | Turbine+generator; calibrated meters |  | Wattmeter + V/I sensors | Power between 10 and 12 kW | Defined | C | Procedure; Datasheet

## Measurements
Timestamp | Test_ID | Sensor | Value | Unit | Baseline_Value | Conditions | Notes | Pass | Rule_Eval
2026-01-22T09:01 | T-001 | coherence | 0.932 |  | Head=7.5m;Flow=45L/s
2026-01-22T09:02 | T-001 | coherence | 0.945 |  | Head=7.5m;Flow=45L/s
2026-01-22T09:03 | T-001 | coherence | 0.917 |  | Head=7.5m;Flow=45L/s
2026-01-22T09:04 | T-001 | coherence | 0.958 |  | Head=7.5m;Flow=45L/s
2026-01-22T09:10 | T-002 | ripple | 7.1 | mm | Baseline=12.4
2026-01-22T09:12 | T-002 | ripple | 6.8 | mm | Baseline=12.5
2026-01-22T09:14 | T-002 | ripple | 7.3 | mm | Baseline=13.1
2026-01-22T09:16 | T-002 | ripple | 6.9 | mm | Baseline=12.8
2026-01-22T09:20 | T-003 | elc drift | 0.045 | Hz | Nominal Load
2026-01-22T09:22 | T-003 | elc drift | 0.062 | Hz | Nominal Load
2026-01-22T09:24 | T-003 | elc drift | 0.088 | Hz | Nominal Load
2026-01-22T09:26 | T-003 | elc drift | 0.091 | Hz | Nominal Load
2026-01-22T09:30 | T-004 | power | 10.5 | kW | Head=7.5m
2026-01-22T09:32 | T-004 | power | 11.3 | kW | Head=7.5m
2026-01-22T09:34 | T-004 | power | 10.8 | kW | Head=7.5m
2026-01-22T09:36 | T-004 | power | 11.9 | kW | Head=7.5m

## Dashboard
Test | Metric | Requirement | Status
T-001 | Coherence >= 0.90 | 0.90 | PASS
T-002 | Ripple Reduction 30-50% | 30-50% | PASS
T-003 | ELC Drift <= 0.1 Hz | 0.1 Hz | PASS
T-004 | Power 10-12 kW | 10-12 kW | PASS

## Trends
Timestamp | ELC Drift
2026-01-22T09:20 | 0.045
2026-01-22T09:22 | 0.062
2026-01-22T09:24 | 0.088
2026-01-22T09:26 | 0.091
Timestamp | Power
2026-01-22T09:30 | 10.5
2026-01-22T09:32 | 11.3
2026-01-22T09:34 | 10.8
2026-01-22T09:36 | 11.9